## Summary
Copyright Philip Haile & Transition Bath 2024

## Scenarios
Flow temperature | Result row | Labour | Radiators | Total | Watts | Percent capacity | COP | Electric kWh | Electric cost | Saving | Additional install cost | Payback
65 | 6 | 0 | 0 | 0 | 12265.8897 | 150.7% | 3.01 | 6013.915 | 1443.3396
50 | 31 | 570 | 632.25 | 1202.25 | 9398.1769 | 115.5% | 3.92 | 4617.8276 | 1108.2786 | 0 | 0
48 | 56 | 570 | 852.28 | 1422.28 | 9316.2833 | 114.5% | 4.03 | 4491.7826 | 1078.0278 | 30.2508 | 220.03 | 7.2735
46 | 81 | 665 | 1326.36 | 1991.36 | 8836.6646 | 108.6% | 4.14 | 4372.4358 | 1049.3846 | 58.894 | 789.11 | 13.3988
44 | 106 | 855 | 1659.44 | 2514.44 | 8613.9845 | 105.8% | 4.25 | 4259.2668 | 1022.224 | 86.0546 | 1312.19 | 15.2483
42 | 131 | 950 | 2007.18 | 2957.18 | 8580.7544 | 105.4% | 4.36 | 4151.8083 | 996.434 | 111.8446 | 1754.93 | 15.6908
40 | 156 | 950 | 2581.3 | 3531.3 | 8416.9899 | 103.4% | 4.47 | 4049.6385 | 971.9132 | 136.3654 | 2329.05 | 17.0795
38 | 181 | 950 | 3227.04 | 4177.04 | 7870.727 | 96.69% | 4.58 | 3952.3764 | 948.5703 | 159.7083 | 2974.79 | 18.6264
36 | 206 | 1045 | 3719.36 | 4764.36 | 7265.6429 | 89.26% | 4.69 | 3859.6768 | 926.3224 | 181.9562 | 3562.11 | 19.5767
Flow temperature | 46

## RadiatorDatabase
Radiator Key | Type | Depth | Height | Length | N | W @ dt 50 | £
ModernxK2x1000x600 | Modern | K2 | 600 | 1000 | 1.3 | 1732 | 99.65
ModernxK2x1000x700 | Modern | K2 | 700 | 1000 | 1.3 | 1961 | 154.36
ModernxK2x1100x600 | Modern | K2 | 600 | 1100 | 1.3 | 1905 | 109.61
ModernxK2x1100x700 | Modern | K2 | 700 | 1100 | 1.3 | 2157 | 181.9
ModernxK2x1200x600 | Modern | K2 | 600 | 1200 | 1.3 | 2078 | 119.57
ModernxK2x1200x700 | Modern | K2 | 700 | 1200 | 1.3 | 2353 | 198.48
ModernxK2x1400x600 | Modern | K2 | 600 | 1400 | 1.3 | 2425 | 154.06
ModernxK2x1400x700 | Modern | K2 | 700 | 1400 | 1.3 | 2745 | 255.64
ModernxK2x1200x450 | Modern | K2 | 450 | 1200 | 1.3 | 1645 | 109.61
ModernxK2x1000x450 | Modern | K2 | 450 | 1000 | 1.3 | 1371 | 91.36
ModernxK2x1100x450 | Modern | K2 | 450 | 1100 | 1.3 | 1508 | 100.52
ModernxK2x1600x600 | Modern | K2 | 600 | 1600 | 1.3 | 2771 | 176.02
ModernxK2x900x450 | Modern | K2 | 450 | 900 | 1.3 | 1234 | 85.67
ModernxK2x1600x700 | Modern | K2 | 700 | 1600 | 1.3 | 3138 | 292.18
ModernxK2x800x450 | Modern | K2 | 450 | 800 | 1.3 | 1097 | 79.19
ModernxK1x700x600 | Modern | K1 | 600 | 700 | 1.3 | 686 | 49.78
ModernxK1x900x600 | Modern | K1 | 600 | 900 | 1.3 | 882 | 64.02
ModernxK1x1200x600 | Modern | K1 | 600 | 1200 | 1.3 | 1176 | 85.36
ModernxK1x600x600 | Modern | K1 | 600 | 600 | 1.3 | 588 | 42.69
ModernxK1x1400x600 | Modern | K1 | 600 | 1400 | 1.3 | 1372 | 99.61
ModernxK1x1600x600 | Modern | K1 | 600 | 1600 | 1.3 | 1568 | 113.84
ModernxK1x1100x600 | Modern | K1 | 600 | 1100 | 1.3 | 1078 | 78.27
ModernxK1x800x600 | Modern | K1 | 600 | 800 | 1.3 | 784 | 56.94
ModernxK1x1000x600 | Modern | K1 | 600 | 1000 | 1.3 | 980 | 71.74
ModernxK2x1600x450 | Modern | K2 | 450 | 1600 | 1.3 | 2194 | 161.37
ModernxK2x1800x450 | Modern | K2 | 450 | 1800 | 1.3 | 2468 | 181.58
ModernxK2x1400x450 | Modern | K2 | 450 | 1400 | 1.3 | 1919 | 141.21
ModernxK2x2000x450 | Modern | K2 | 450 | 2000 | 1.3 | 2742 | 209.8
ModernxK2x700x450 | Modern | K2 | 450 | 700 | 1.3 | 960 | 74.6
ModernxK2x1800x600 | Modern | K2 | 600 | 1800 | 1.3 | 3118 | 198.04
ModernxK2x1800x700 | Modern | K2 | 700 | 1800 | 1.3 | 3530 | 328.68
ModernxK1x1800x600 | Modern | K1 | 600 | 1800 | 1.3 | 1764 | 139.06
ModernxK1x500x600 | Modern | K1 | 600 | 500 | 1.3 | 490 | 40.66
ModernxK2x600x450 | Modern | K2 | 450 | 600 | 1.3 | 823 | 68.5
ModernxK2x2000x600 | Modern | K2 | 600 | 2000 | 1.3 | 3464 | 303.12
ModernxK2x2000x700 | Modern | K2 | 700 | 2000 | 1.3 | 3922 | 379.84
ModernxK2x2200x600 | Modern | K2 | 600 | 2200 | 1.3 | 3810 | 378.33
ModernxK2x2200x450 | Modern | K2 | 450 | 2200 | 1.3 | 3016 | 257.01
ModernxK2x2400x450 | Modern | K2 | 450 | 2400 | 1.3 | 3290 | 280.38
ModernxK1x1100x450 | Modern | K1 | 450 | 1100 | 1.3 | 832 | 71.74
ModernxK1x800x450 | Modern | K1 | 450 | 800 | 1.3 | 605 | 52.17
ModernxK1x1600x450 | Modern | K1 | 450 | 1600 | 1.3 | 1210 | 104.34
ModernxK1x600x450 | Modern | K1 | 450 | 600 | 1.3 | 454 | 39.15
ModernxK1x1000x450 | Modern | K1 | 450 | 1000 | 1.3 | 756 | 65.2
ModernxK1x1400x450 | Modern | K1 | 450 | 1400 | 1.3 | 1058 | 91.29
ModernxK1x900x450 | Modern | K1 | 450 | 900 | 1.3 | 680 | 58.68
ModernxK1x700x450 | Modern | K1 | 450 | 700 | 1.3 | 529 | 45.65
ModernxK1x1200x450 | Modern | K1 | 450 | 1200 | 1.3 | 907 | 78.27
ModernxK2x1000x300 | Modern | K2 | 300 | 1000 | 1.3 | 982 | 85.18
ModernxK2x2400x600 | Modern | K2 | 600 | 2400 | 1.3 | 4157 | 412.94
ModernxK2x400x600 | Modern | K2 | 600 | 400 | 1.3 | 693 | 58.14
ModernxK2x1500x300 | Modern | K2 | 300 | 1500 | 1.3 | 1473 | 130.91
ModernxK2x500x450 | Modern | K2 | 450 | 500 | 1.3 | 686 | 61.83
ModernxK2x400x700 | Modern | K2 | 700 | 400 | 1.3 | 784 | 96.46
ModernxK2x2000x300 | Modern | K2 | 300 | 2000 | 1.3 | 1964 | 181.53
ModernxK2x500x600 | Modern | K2 | 600 | 500 | 1.3 | 866 | 67.49
ModernxK2x500x700 | Modern | K2 | 700 | 500 | 1.3 | 981 | 111.95
ModernxK2x600x600 | Modern | K2 | 600 | 600 | 1.3 | 1039 | 74.74
ModernxK1x400x600 | Modern | K1 | 600 | 400 | 1.3 | 392 | 36.62
ModernxP+x1000x300 | Modern | P+ | 300 | 1000 | 1.3 | 745 | 71.74
ModernxK2x600x700 | Modern | K2 | 700 | 600 | 1.3 | 1177 | 124.02
ModernxK2x400x450 | Modern | K2 | 450 | 400 | 1.3 | 548 | 53.29
ModernxK2x700x600 | Modern | K2 | 600 | 700 | 1.3 | 1212 | 81.84
ModernxK3x1200x500 | Modern | K3 | 500 | 1200 | 1.3 | 2467 | 243
ModernxP+x1000x700 | Modern | P+ | 700 | 1000 | 1.3 | 1530 | 150.74
ModernxK3x1100x600 | Modern | K3 | 600 | 1100 | 1.3 | 2628 | 259
ModernxK1x500x450 | Modern | K1 | 450 | 500 | 1.3 | 378 | 37.26
ModernxK3x1100x500 | Modern | K3 | 500 | 1100 | 1.3 | 2262 | 223
ModernxK3x1200x600 | Modern | K3 | 600 | 1200 | 1.3 | 2867 | 283
ModernxK3x1000x500 | Modern | K3 | 500 | 1000 | 1.3 | 2056 | 203
ModernxK3x1000x600 | Modern | K3 | 600 | 1000 | 1.3 | 2389 | 236
ModernxP+x1200x700 | Modern | P+ | 700 | 1200 | 1.3 | 1836 | 181.86
ModernxK2x700x700 | Modern | K2 | 700 | 700 | 1.3 | 1373 | 135.04
ModernxK2x800x600 | Modern | K2 | 600 | 800 | 1.3 | 1386 | 86.36
ModernxK1x2000x600 | Modern | K1 | 600 | 2000 | 1.3 | 1960 | 195.09
ModernxK2x500x300 | Modern | K2 | 300 | 500 | 1.3 | 491 | 48.99
ModernxK1x1500x300 | Modern | K1 | 300 | 1500 | 1.3 | 764 | 76.23
ModernxP+x900x700 | Modern | P+ | 700 | 900 | 1.3 | 1377 | 137.73
ModernxP+x800x700 | Modern | P+ | 700 | 800 | 1.3 | 1224 | 124.55
ModernxK3x900x500 | Modern | K3 | 500 | 900 | 1.3 | 1850 | 190
ModernxK3x900x600 | Modern | K3 | 600 | 900 | 1.3 | 2150 | 221
ModernxP+x700x700 | Modern | P+ | 700 | 700 | 1.3 | 1071 | 112.74
ModernxK1x1000x300 | Modern | K1 | 300 | 1000 | 1.3 | 509 | 53.62
ModernxK2x800x700 | Modern | K2 | 700 | 800 | 1.3 | 1569 | 143.31
ModernxK1x800x700 | Modern | K1 | 700 | 800 | 1.3 | 894 | 94.46
ModernxK1x1100x700 | Modern | K1 | 700 | 1100 | 1.3 | 1229 | 129.87
ModernxK1x700x700 | Modern | K1 | 700 | 700 | 1.3 | 782 | 82.64
ModernxK1x1000x700 | Modern | K1 | 700 | 1000 | 1.3 | 1117 | 118.06
ModernxK1x600x700 | Modern | K1 | 700 | 600 | 1.3 | 670 | 70.82
ModernxK1x1400x700 | Modern | K1 | 700 | 1400 | 1.3 | 1564 | 165.32
ModernxK1x1600x700 | Modern | K1 | 700 | 1600 | 1.3 | 1787 | 188.91
ModernxK1x1200x700 | Modern | K1 | 700 | 1200 | 1.3 | 1340 | 141.69
ModernxK1x900x700 | Modern | K1 | 700 | 900 | 1.3 | 1005 | 106.28
ModernxP+x1400x700 | Modern | P+ | 700 | 1400 | 1.3 | 2142 | 227.63
ModernxK3x800x600 | Modern | K3 | 600 | 800 | 1.3 | 1911 | 204
ModernxK3x800x500 | Modern | K3 | 500 | 800 | 1.3 | 1645 | 176
ModernxK1x2400x600 | Modern | K1 | 600 | 2400 | 1.3 | 2352 | 253.72
ModernxK1x2200x600 | Modern | K1 | 600 | 2200 | 1.3 | 2156 | 232.65
ModernxP+x1100x700 | Modern | P+ | 700 | 1100 | 1.3 | 1683 | 181.86
ModernxK1x2400x450 | Modern | K1 | 450 | 2400 | 1.3 | 1814 | 196.23
ModernxP+x600x700 | Modern | P+ | 700 | 600 | 1.3 | 918 | 99.86
ModernxK3x1800x500 | Modern | K3 | 500 | 1800 | 1.3 | 3701 | 403
ModernxK3x1800x600 | Modern | K3 | 600 | 1800 | 1.3 | 4300 | 469
ModernxK3x1400x500 | Modern | K3 | 500 | 1400 | 1.3 | 2878 | 314
ModernxK3x1600x600 | Modern | K3 | 600 | 1600 | 1.3 | 3822 | 417
ModernxK3x1400x600 | Modern | K3 | 600 | 1400 | 1.3 | 3345 | 365
ModernxK3x1600x500 | Modern | K3 | 500 | 1600 | 1.3 | 3290 | 359
ModernxK1x400x450 | Modern | K1 | 450 | 400 | 1.3 | 302 | 33.53
ModernxK1x1800x450 | Modern | K1 | 450 | 1800 | 1.3 | 1361 | 154.74
ModernxK2x900x600 | Modern | K2 | 600 | 900 | 1.3 | 1559 | 93.42
ModernxK1x1800x700 | Modern | K1 | 700 | 1800 | 1.3 | 2011 | 230.73
ModernxK3x700x500 | Modern | K3 | 500 | 700 | 1.3 | 1439 | 166
ModernxK3x700x600 | Modern | K3 | 600 | 700 | 1.3 | 1672 | 193
ModernxK1x2000x450 | Modern | K1 | 450 | 2000 | 1.3 | 1512 | 175.38
ModernxP+x1500x300 | Modern | P+ | 300 | 1500 | 1.3 | 1118 | 130.16
ModernxP+x500x300 | Modern | P+ | 300 | 500 | 1.3 | 373 | 44.15
ModernxK3x1100x700 | Modern | K3 | 700 | 1100 | 1.3 | 2983 | 355
ModernxK3x1000x700 | Modern | K3 | 700 | 1000 | 1.3 | 2712 | 323
ModernxK3x1200x700 | Modern | K3 | 700 | 1200 | 1.3 | 3254 | 388
ModernxP+x400x700 | Modern | P+ | 700 | 400 | 1.3 | 612 | 72.98
ModernxK1x2000x700 | Modern | K1 | 700 | 2000 | 1.3 | 2234 | 266.62
ModernxK1x500x700 | Modern | K1 | 700 | 500 | 1.3 | 559 | 67.47
ModernxP+x500x700 | Modern | P+ | 700 | 500 | 1.3 | 765 | 92.68
ModernxK2x900x700 | Modern | K2 | 700 | 900 | 1.3 | 1765 | 155.07
ModernxK3x600x600 | Modern | K3 | 600 | 600 | 1.3 | 1433 | 177
ModernxK3x600x500 | Modern | K3 | 500 | 600 | 1.3 | 1234 | 152.51
ModernxK3x900x700 | Modern | K3 | 700 | 900 | 1.3 | 2441 | 303
ModernxK1x500x300 | Modern | K1 | 300 | 500 | 1.3 | 255 | 32.85
ModernxK3x800x700 | Modern | K3 | 700 | 800 | 1.3 | 2170 | 280
ModernxK1x2200x450 | Modern | K1 | 450 | 2200 | 1.3 | 1663 | 218.4
ModernxK3x1600x700 | Modern | K3 | 700 | 1600 | 1.3 | 4339 | 571
ModernxK3x1400x700 | Modern | K3 | 700 | 1400 | 1.3 | 3797 | 500
ModernxK3x1800x700 | Modern | K3 | 700 | 1800 | 1.3 | 4882 | 643
ModernxK3x500x600 | Modern | K3 | 600 | 500 | 1.3 | 1195 | 160
ModernxK1x400x700 | Modern | K1 | 700 | 400 | 1.3 | 447 | 60.71
ModernxK3x2000x700 | Modern | K3 | 700 | 2000 | 1.3 | 5424 | 743
ModernxK3x700x700 | Modern | K3 | 700 | 700 | 1.3 | 1898 | 264
ModernxK3x400x600 | Modern | K3 | 600 | 400 | 1.3 | 956 | 137
ModernxK3x600x700 | Modern | K3 | 700 | 600 | 1.3 | 1627 | 242
ModernxK3x1000x300 | Modern | K3 | 300 | 1000 | 1.3 | 1349 | 201
ModernxK3x2400x500 | Modern | K3 | 500 | 2400 | 1.3 | 4934 | 741
ModernxK3x2000x600 | Modern | K3 | 600 | 2000 | 1.3 | 4778 | 718
ModernxK3x2000x500 | Modern | K3 | 500 | 2000 | 1.3 | 4112 | 618
ModernxK3x2400x600 | Modern | K3 | 600 | 2400 | 1.3 | 5734 | 862
ModernxK3x2000x300 | Modern | K3 | 300 | 2000 | 1.3 | 2698 | 428
ModernxK3x500x700 | Modern | K3 | 700 | 500 | 1.3 | 1356 | 219

## RadiatorLocations
Room Name | Location | Length | Height | Type | Depth | Labour Cost | Existing Radiator | Status | Database check | Status
Lounge | Loc1 | 1800 | 600 | Modern | K3 | 95 | ModernxK2x900x600 | Replace&Move | ModernxK2x900x600 | Replace
Lounge | Loc2 | 2000 | 700 | Modern | K3 | 95 | ModernxK2x900x600 | Retain | ModernxK2x900x600 | Replace&Move
Dining | Loc1 | 1600 | 900 | Modern | K3 | 95 | ModernxK2x1200x600 | Retain | ModernxK2x1200x600 | Retain
Kitchen | Loc1 | 1700 | 700 | Modern | K3 | 95 | ModernxK2x1200x600 | Retain | ModernxK2x1200x600 | Available Space
Utility | Loc1 | 1000 | 700 | Modern | K3 | 95 | ModernxK1x600x700 | Retain | ModernxK1x600x700
Hall | Loc1 | 1500 | 600 | Modern | K3 | 95 | ModernxK2x1000x600 | Retain | ModernxK2x1000x600
Hall | Loc2 | 1000 | 600 | Modern | K3 | 95 | ModernxK1x600x700 | Retain | ModernxK1x600x700
Bath | Loc1 | 1000 | 600 | Modern | K3 | 95 | ModernxK1x900x700 | Retain | ModernxK1x900x700
Bed SW | Loc1 | 1800 | 700 | Modern | K3 | 95 | ModernxK2x1000x600 | Retain | ModernxK2x1000x600
Bed NW | Loc1 | 1800 | 700 | Modern | K3 | 95 | ModernxK2x700x600 | Retain | ModernxK2x700x600
Bed N | Loc1 | 1800 | 700 | Modern | K3 | 95 | ModernxK1x800x600 | Retain | ModernxK1x800x600
Main bed | Loc1 | 1000 | 600 | Modern | K3 | 95 | ModernxK1x900x600 | Retain | ModernxK1x900x600
Ensuite | Loc1 | 1000 | 600 | Modern | K3 | 95 | ModernxK1x600x600 | Retain | ModernxK1x600x600

## CalcResults
Libraries | 0 | # these python objects need to be kept on this page otherwise dependency gets lost after save and reload (Excel bug)
Radiators | 0
Rooms | 0
Home | 0
Load Tables | #VALUE!
65 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK2x900x600 | 0 | 0 | Original | 1262.0911
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK2x900x600 | 0 | 0 | Original | 1262.0911
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK2x1200x600 | 0 | 0 | Original | 1630.9741
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK2x1200x600 | 0 | 0 | Original | 1785.8811
| Hall | Loc1 | ModernxK2x1000x600 | 0 | 0 | 0 | Removed | 0
| Hall | Loc2 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 575.8135
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 575.8135
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK1x900x600 | 0 | 0 | Original | 758.0111
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK1x800x600 | 0 | 0 | Original | 673.7877
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x700x600 | 0 | 0 | Original | 1041.6208
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 1488.5208
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK1x600x600 | 0 | 0 | Original | 447.1033
| Bath | Loc1 | ModernxK1x900x700 | ModernxK1x900x700 | 0 | 0 | Original | 764.1816
50 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK2x900x600 | 0 | 0 | Original | 716.6673
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK2x1600x700 | 292.18 | 95 | Replaced | 1442.5286
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK2x1400x600 | 154.06 | 95 | Replaced | 1062.3567
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK2x1200x600 | 0 | 0 | Original | 1046.5336
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 872.2792
| Hall | Loc2 | ModernxK1x600x700 | 0 | 0 | 0 | Removed | 0
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 337.429
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK2x800x600 | 86.36 | 95 | Replaced | 698.0248
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK1x800x600 | 0 | 0 | Original | 394.8423
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1200x600 | 0 | 95 | Moved:Dining:Loc1 | 865.9379
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 872.2792
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK1x900x600 | 0 | 95 | Moved:Main bed:Loc1 | 367.5444
| Bath | Loc1 | ModernxK1x900x700 | ModernxK2x1000x600 | 99.65 | 95 | Replaced | 721.7539
48 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK2x900x600 | 0 | 0 | Original | 649.6618
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK2x2000x700 | 379.84 | 95 | Replaced | 1634.3641
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK2x1600x600 | 176.02 | 95 | Replaced | 1096.2041
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK2x1200x600 | 0 | 0 | Original | 955.25
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 796.1949
| Hall | Loc2 | ModernxK1x600x700 | 0 | 0 | 0 | Removed | 0
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 307.9969
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK2x900x600 | 93.42 | 95 | Replaced | 716.6673
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK1x800x600 | 0 | 0 | Original | 360.4023
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1200x600 | 0 | 95 | Moved:Dining:Loc1 | 778.7046
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 796.1949
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK2x700x600 | 0 | 95 | Moved:Bed NW:Loc1 | 454.1819
| Bath | Loc1 | ModernxK1x900x700 | ModernxK3x1000x500 | 203 | 95 | Replaced | 770.4604
46 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK2x900x600 | 0 | 0 | Original | 584.2158
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK3x1800x600 | 469 | 95 | Replaced | 1611.3715
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK3x1200x600 | 283 | 95 | Replaced | 1015.3224
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK2x1400x600 | 154.06 | 95 | Replaced | 1010.5388
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 721.7539
| Hall | Loc2 | ModernxK1x600x700 | 0 | 0 | 0 | Removed | 0
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 279.2004
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK2x1000x600 | 99.65 | 95 | Replaced | 721.7539
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK1x800x600 | 0 | 0 | Original | 326.7061
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1000x600 | 99.65 | 95 | Replaced | 721.7539
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 721.7539
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK2x700x600 | 0 | 95 | Moved:Bed NW:Loc1 | 404.5867
| Bath | Loc1 | ModernxK1x900x700 | ModernxK3x900x600 | 221 | 95 | Replaced | 717.7074
44 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK2x1800x600 | 198.04 | 95 | Replaced | 1040.8427
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK2x2000x600 | 303.12 | 95 | Replaced | 1156.3435
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK3x1600x500 | 359 | 95 | Replaced | 1032.3214
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK2x1400x600 | 154.06 | 95 | Replaced | 908.7386
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 649.0454
| Hall | Loc2 | ModernxK1x600x700 | 0 | 0 | 0 | Removed | 0
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 251.0742
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK3x900x500 | 190 | 95 | Replaced | 693.2645
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK1x800x600 | 0 | 0 | Original | 293.7942
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1100x600 | 109.61 | 95 | Replaced | 713.875
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1100x600 | 109.61 | 95 | Replaced | 713.875
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK2x900x600 | 0 | 95 | Moved:Lounge:Loc1 | 458.3847
| Bath | Loc1 | ModernxK1x900x700 | ModernxK3x1000x600 | 236 | 95 | Replaced | 702.4253
42 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK2x1800x600 | 198.04 | 95 | Replaced | 916.7694
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK3x1800x600 | 469 | 95 | Replaced | 1264.3067
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK3x1600x600 | 417 | 95 | Replaced | 1049.4287
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK2x1600x600 | 176.02 | 95 | Replaced | 925.0081
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 578.1718
| Hall | Loc2 | ModernxK1x600x700 | 0 | 0 | 0 | Removed | 0
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 223.6577
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK3x1000x500 | 203 | 95 | Replaced | 686.3286
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK2x700x600 | 0 | 95 | Moved:Bed NW:Loc1 | 309.593
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1400x600 | 154.06 | 95 | Replaced | 809.5072
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1400x600 | 154.06 | 95 | Replaced | 809.5072
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK2x900x600 | 0 | 95 | Moved:Lounge:Loc1 | 398.2305
| Bath | Loc1 | ModernxK1x900x700 | ModernxK3x1000x600 | 236 | 95 | Replaced | 610.2455
40 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK3x1800x600 | 469 | 95 | Replaced | 1098.3909
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK3x1800x600 | 469 | 95 | Replaced | 1098.3909
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK3x1600x700 | 571 | 95 | Replaced | 1026.7336
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK2x1600x700 | 292.18 | 95 | Replaced | 922.6499
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 509.251
| Hall | Loc2 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 196.9966
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 196.9966
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK3x1000x600 | 236 | 95 | Replaced | 702.4253
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK2x900x600 | 0 | 95 | Moved:Lounge:Loc1 | 340.1076
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1400x600 | 154.06 | 95 | Replaced | 713.0102
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1400x600 | 154.06 | 95 | Replaced | 713.0102
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK2x1000x600 | 0 | 95 | Moved:Bed SW:Loc1 | 377.8488
| Bath | Loc1 | ModernxK1x900x700 | ModernxK3x1000x600 | 236 | 95 | Replaced | 521.1783
38 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK3x1800x600 | 469 | 95 | Replaced | 938.0774
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK3x2000x700 | 743 | 95 | Replaced | 1183.2864
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK3x1600x700 | 571 | 95 | Replaced | 867.9747
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK3x1600x600 | 417 | 95 | Replaced | 976.2907
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 442.4216
| Hall | Loc2 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 171.1446
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 171.1446
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK3x1000x600 | 236 | 95 | Replaced | 610.2455
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK2x900x600 | 0 | 95 | Moved:Lounge:Loc1 | 284.1967
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1600x600 | 176.02 | 95 | Replaced | 707.8235
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1600x600 | 176.02 | 95 | Replaced | 707.8235
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK3x1000x500 | 203 | 95 | Replaced | 374.7969
| Bath | Loc1 | ModernxK1x900x700 | ModernxK3x1000x600 | 236 | 95 | Replaced | 435.5009
36 | Room Name | Location name | Originally | Proposed Radiator | £ | Labour Cost | Status | Watts
| Lounge | Loc1 | ModernxK2x900x600 | ModernxK3x1800x600 | 469 | 95 | Replaced | 783.8651
| Lounge | Loc2 | ModernxK2x900x600 | ModernxK3x2000x700 | 743 | 95 | Replaced | 988.7638
| Dining | Loc1 | ModernxK2x1200x600 | ModernxK3x1600x700 | 571 | 95 | Replaced | 715.6681
| Kitchen | Loc1 | ModernxK2x1200x600 | ModernxK3x1600x700 | 571 | 95 | Replaced | 946.5855
| Hall | Loc1 | ModernxK2x1000x600 | ModernxK2x1000x600 | 0 | 0 | Original | 377.8488
| Hall | Loc2 | ModernxK1x600x700 | ModernxK2x900x600 | 0 | 95 | Moved:Lounge:Loc1 | 230.7238
| Utility | Loc1 | ModernxK1x600x700 | ModernxK1x600x700 | 0 | 0 | Original | 146.1655
| Main bed | Loc1 | ModernxK1x900x600 | ModernxK3x1000x600 | 236 | 95 | Replaced | 521.1783
| Bed N | Loc1 | ModernxK1x800x600 | ModernxK2x1200x600 | 0 | 95 | Moved:Dining:Loc1 | 307.533
| Bed NW | Loc1 | ModernxK2x700x600 | ModernxK2x1800x700 | 328.68 | 95 | Replaced | 770.0961
| Bed SW | Loc1 | ModernxK2x1000x600 | ModernxK2x1800x700 | 328.68 | 95 | Replaced | 770.0961
| Ensuite | Loc1 | ModernxK1x600x600 | ModernxK3x1000x600 | 236 | 95 | Replaced | 353.5594
| Bath | Loc1 | ModernxK1x900x700 | ModernxK3x1000x600 | 236 | 95 | Replaced | 353.5594

## Rooms
Room Name | Heat Loss | Room Temperature | Room | 65 | 50 | 48 | 46 | 44 | 42 | 40 | 38 | 36 | Room | 65 | 50 | 48 | 46 | 44 | 42 | 40 | 38 | 36 | Room | 65 | 50 | 48 | 46 | 44 | 42 | 40 | 38 | 36
Lounge | 2151 | 20 | Lounge | 2524.1823 | 2159.1959 | 2284.0259 | 2195.5873 | 2197.1862 | 2181.0761 | 2196.7817 | 2121.3638 | 1772.629 | Lounge | 117.3% | 100.4% | 106.2% | 102.1% | 102.1% | 101.4% | 102.1% | 98.62% | 82.41% | Lounge | 0 | 387.18 | 474.84 | 564 | 691.16 | 857.04 | 1128 | 1402 | 1402
Dining | 1014 | 21 | Dining | 1630.9741 | 1062.3567 | 1096.2041 | 1015.3224 | 1032.3214 | 1049.4287 | 1026.7336 | 867.9747 | 715.6681 | Dining | 160.8% | 104.8% | 108.1% | 100.1% | 101.8% | 103.5% | 101.3% | 85.6% | 70.58% | Dining | 0 | 249.06 | 271.02 | 378 | 454 | 512 | 666 | 666 | 666
Kitchen | 886 | 18 | Kitchen | 1785.8811 | 1046.5336 | 955.25 | 1010.5388 | 908.7386 | 925.0081 | 922.6499 | 976.2907 | 946.5855 | Kitchen | 201.6% | 118.1% | 107.8% | 114.1% | 102.6% | 104.4% | 104.1% | 110.2% | 106.8% | Kitchen | 0 | 0 | 0 | 249.06 | 249.06 | 271.02 | 387.18 | 512 | 666
Hall | 564 | 18 | Hall | 575.8135 | 872.2792 | 796.1949 | 721.7539 | 649.0454 | 578.1718 | 706.2476 | 613.5662 | 608.5726 | Hall | 102.1% | 154.7% | 141.2% | 128% | 115.1% | 102.5% | 125.2% | 108.8% | 107.9% | Hall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95
Utility | 115 | 18 | Utility | 575.8135 | 337.429 | 307.9969 | 279.2004 | 251.0742 | 223.6577 | 196.9966 | 171.1446 | 146.1655 | Utility | 500.7% | 293.4% | 267.8% | 242.8% | 218.3% | 194.5% | 171.3% | 148.8% | 127.1% | Utility | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Main bed | 684 | 18 | Main bed | 758.0111 | 698.0248 | 716.6673 | 721.7539 | 693.2645 | 686.3286 | 702.4253 | 610.2455 | 521.1783 | Main bed | 110.8% | 102.1% | 104.8% | 105.5% | 101.4% | 100.3% | 102.7% | 89.22% | 76.2% | Main bed | 0 | 181.36 | 188.42 | 194.65 | 285 | 298 | 331 | 331 | 331
Bed N | 271 | 18 | Bed N | 673.7877 | 394.8423 | 360.4023 | 326.7061 | 293.7942 | 309.593 | 340.1076 | 284.1967 | 307.533 | Bed N | 248.6% | 145.7% | 133% | 120.6% | 108.4% | 114.2% | 125.5% | 104.9% | 113.5% | Bed N | 0 | 0 | 0 | 0 | 0 | 95 | 95 | 95 | 95
Bed NW | 695 | 18 | Bed NW | 1041.6208 | 865.9379 | 778.7046 | 721.7539 | 713.875 | 809.5072 | 713.0102 | 707.8235 | 770.0961 | Bed NW | 149.9% | 124.6% | 112% | 103.8% | 102.7% | 116.5% | 102.6% | 101.8% | 110.8% | Bed NW | 0 | 95 | 95 | 194.65 | 204.61 | 249.06 | 249.06 | 271.02 | 423.68
Bed SW | 694 | 18 | Bed SW | 1488.5208 | 872.2792 | 796.1949 | 721.7539 | 713.875 | 809.5072 | 713.0102 | 707.8235 | 770.0961 | Bed SW | 214.5% | 125.7% | 114.7% | 104% | 102.9% | 116.6% | 102.7% | 102% | 111% | Bed SW | 0 | 0 | 0 | 0 | 204.61 | 249.06 | 249.06 | 271.02 | 423.68
Ensuite | 362 | 22 | Ensuite | 447.1033 | 367.5444 | 454.1819 | 404.5867 | 458.3847 | 398.2305 | 377.8488 | 374.7969 | 353.5594 | Ensuite | 123.5% | 101.5% | 125.5% | 111.8% | 126.6% | 110% | 104.4% | 103.5% | 97.67% | Ensuite | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 298 | 331
Bath | 704 | 22 | Bath | 764.1816 | 721.7539 | 770.4604 | 717.7074 | 702.4253 | 610.2455 | 521.1783 | 435.5009 | 353.5594 | Bath | 108.5% | 102.5% | 109.4% | 101.9% | 99.78% | 86.68% | 74.03% | 61.86% | 50.22% | Bath | 0 | 194.65 | 298 | 316 | 331 | 331 | 331 | 331 | 331
|  |  | Row offset | 6 | 31 | 56 | 81 | 106 | 131 | 156 | 181 | 206

## Calcs
Total Heat Loss | 8140 | W
Average temperature | 19.426 | C
Annual | 18101.884 | kWh
Tariff | 0.24 | £/kWh

## Examples
150
7.9688

## Design
Suggested upgrades at each flow temperature
Room | Room Heat Loss at -2C | Set Temperature | 55 | 50 | 45 | 40 | 35
Hall | 300W | 18C | R: K2x600x600, R: K1x600x600 | R:K2x600x600, >:K2x1000x600 | R:K2x600x600, >:K2x1000x600 | R:K2x600x600, >:K2x1000x600 | +:K3x600x600, >:K2x1000x600
Lounge | 2000W | 21C | R: K2x1000x600, R: K2x1000x600 | R: K2x1000x600, +: K2x1000x600 | R: K2x1000x600, +: K2x1000x600 | R: K2x1000x600, +: K2x1000x600 | R: K2x1000x600, +: K2x1000x600
Kitchen | 1500W | 18C | R: K3x1400x600 | R: K3x1400x600 | >:K3x1600x600 | >:K3x1600x600 | >:K3x1600x600
Dining | 1200W | 18C | R: K2x1200x600 | R: K2x1200x600 | <: K2x1200x600 | <: K2x1200x600 | <: K2x1200x600
Utility | 300W | 18C | R: K2x400x600 | R: K2x400x600 | R: K2x400x600 | +: K2x600x600 | +: K2x600x600
Main bed | 500W | 18C | R: K2x1200x600 | R: K2x1200x600 | R: K2x1200x600 | <: K2x1200x600 | <: K2x1200x600
Bed 2 | 400W | 18C | R: K2x1200x600 | R: K2x1200x600 | R: K2x1200x600 | R: K2x1200x600 | +: K2x1200x600
Bed 3 | 300W | 18C | R: K2x600x600 | R: K2x600x600 | R: K2x600x600 | +: K2x800x600 | +: K2x800x600
Bed 4 | 300W | 18C | R: K2x600x600 | R: K2x600x600 | R: K2x600x600 | R: K2x600x600 | R: K2x600x600
Bath | 400W | 22C | R: K2x800x600 | R: TheoDesigner2x1700x550 | R: TheoDesigner2x1700x550 | R: TheoDesigner2x1700x550 | R: TheoDesigner2x1700x550
Ensuite | 400W | 22C | R: TheoDesigner2x1700x550 | R: TheoDesigner2x1700x550 | R: TheoDesigner2x1700x550 | R: TheoDesigner2x1700x550 | R: TheoDesigner2x1700x550
Radiator cost |  |  | 0 | 500 | 800 | 1200 | 1500
Labour cost |  |  |  | 150 | 300 | 400 | 450
Total cost |  |  |  | 650 | 1100 | 1600 | 1950
Efficiency (SCOP) |  |  | 3.42 | 3.78 | 4.14 | 4.49 | 4.84
Annual Costs |  |  | 1169.5906 | 1058.2011 | 966.1836 | 890.8686 | 826.4463
Saving |  |  |  | 111.3896 | 203.4071 | 278.722 | 343.1444
Payback (years) |  |  |  | 5.8354 | 5.4079 | 5.7405 | 5.6827
Key
R: | Retain existing
+ | a new additional radiator (in addition to existing radiators)
> | a new replacement radiator (existing radiator removed)
< | A replacement radiator moved from one replaced elsewhere in home
^ | An additional radiator moved from one replaced elsewhere in home

## Tabular
| K1 | K1 | K1 | K1 | P+ | P+ | K2 | K2 | K2 | K2 | K3 | K3 | K3 | K3
Watts | 300 | 450 | 600 | 700 | 300 | 700 | 300 | 450 | 600 | 700 | 300 | 450 | 600 | 700
| K1x300 | K1x450 | K1x600 | K1x700 | P+x300 | P+x700 | K2x300 | K2x450 | K2x600 | K2x700 | K3x300 | K3x450 | K3x600 | K3x700
300
400
500
600
700
800
900
1000
1100
1200
1400
1600
1800
2000
2200
2400
2600
2800
3000
| K1 | K1 | K1 | K1 | P+ | P+ | K2 | K2 | K2 | K2 | K3 | K3 | K3 | K3
£ | 300 | 450 | 600 | 700 | 300 | 700 | 300 | 450 | 600 | 700 | 300 | 450 | 600 | 700
| K1x300 | K1x450 | K1x600 | K1x700 | P+x300 | P+x700 | K2x300 | K2x450 | K2x600 | K2x700 | K3x300 | K3x450 | K3x600 | K3x700
300
400
500
600
700
800
900
1000
1100
1200
1400
1600
1800
2000
2200
2400
2600
2800
3000
| K1 | K1 | K1 | K1 | P+ | P+ | K2 | K2 | K2 | K2 | K3 | K3 | K3 | K3
W/£ | 300 | 450 | 600 | 700 | 300 | 700 | 300 | 450 | 600 | 700 | 300 | 450 | 600 | 700
| K1x300 | K1x450 | K1x600 | K1x700 | P+x300 | P+x700 | K2x300 | K2x450 | K2x600 | K2x700 | K3x300 | K3x450 | K3x600 | K3x700
300
400
500
600
700
800
900
1000
1100
1200
1400
1600
1800
2000
2200
2400
2600
2800
3000

## Form
Room Name | Length | Height | Type | Max Subtype | Existing Radiator | Condition
Lounge | 1500 | 600 | Modern | K2 | ModernxK2x600x450 | Good
Lounge
Lounge
Dining